## Slide 1: Pumps and Pumping Systems
Types
Performance evaluation
Efficient system operation
Flow control strategies
Energy conservation opportunities

## Slide 2: Pumps and Pumping Systems
Centrifugal Pumps

## Slide 3: Pump Performance Curve

## Slide 4: Hydraulic power, pump shaft power and electrical input power
Hydraulic power Ph = Q (m3/s) x Total head, hd - hs (m) x  (kg/m3) x g (m2/s) 1000
Where hd - discharge head, hs – suction head,  - density of the fluid, g – acceleration due to gravity
Pump shaft power Ps = Hydraulic power, Ph pump efficiency, Pump
Electrical input power = Pump shaft power P Motor

## Slide 5: System Characteristics
Static Head
Static Head vs. Flow

## Slide 6: Dynamic (Friction) Head
Friction Head vs. Flow

## Slide 7: System with high static head

## Slide 8: System with low static head

## Slide 9: Pump curve

## Slide 10: Pump operating point

## Slide 11: Typical pump characteristic curves

## Slide 12: Selecting a pump
Head
Meters
System Curve
Flow (m
3
/hr)

## Slide 13: Selecting a pump
Head
Meters
82%
Pump Curve at
Const. Speed
System Curve
Flow (m
3
/hr)
Operating Point
500 m3/hr

## Slide 14: Selecting a pump
Head,
m
82%
Pump Curve at
Const. Speed
System Curve
Flow (m
3
/hr)
Operating Point
500
300
50

## Slide 15: Selecting a pump
Pump Efficiency
77%
82%
Pump Curve at
Const. Speed
Partially
closed valve
Full open valve
System Curves
Flow (m
3
/hr)
500
300
Head,
m
50
70

## Slide 16: Selecting a pump
Head
Meters
Pump Efficiency 77%
82%
Pump Curve at
Const. Speed
Partially
closed valve
Full open valve
System Curves
Flow (m
3
/hr)
Operating Points
A
B
500 m
3
/hr
300 m
3
/hr
50 m
70 m
Static
Head
C
42 m

## Slide 17: Efficiency Curves
28.6 kW
14.8 kW
Notes: 17
Use the white board and do the following
Assume that we need to pump 68 m3/hr. to a 47 meter head with a pump that is 60% efficient at that point.
Liquid Power - 68 x 47 / 360 = 8.9 Kw
Where ‘360’ is a constant
Shaft Power - 8.9 / 0.60 = 14.8 Kw
Where 0.6 is the efficiency at that point
Motor Power - 14.8 / 0.9 = 16.4 Kw
Where 0.9 is the motor efficiency
As shown in the drawing, we should be using impeller "E" to do this, but we have an oversized pump so we are using the larger impeller "A" with the pump discharge valve throttled back to 68 cubic meters per hour, giving us an actual head of 76 meters.
Now our Kilowatts look like this:
68 x 76 / 360 = 14.3 Kw being produced by the pump, and 14.3 / 0.50 = 28.6 Kw required to do this. Subtracting the amount of kilowatts we should have been using gives us: 28.6 - 14.8 = 13.8 extra kilowatts being used to pump against the throttled discharge valve.
Extra energy used - 8760 hrs/yr x 13.8 = 120,880 kw.
= $ 10,000/annum
In this example the extra cost of the electricity could almost equal the cost of purchasing two or three pumps.

## Slide 18: If we select E, then the pump efficiency is 60%
Hydraulic Power = Q (m3/s) x Total head, hd - hs (m) x  (kg/m3) x g (m2/s) 1000
= (68/3600) x 47 x 1000 x 9.81
1000
= 8.7 kW
Shaft Power - 8.7 / 0.60 = 14.5 Kw
Motor Power - 14.8 / 0.9 = 16.1Kw (considering a motor efficiency of 90%)

## Slide 19: If we select A, then the pump efficiency is 50%
Hydraulic Power = Q (m3/s) x Total head, hd - hs (m) x  (kg/m3) x g (m2/s) 1000
(68/3600) x 76 x 1000 x 9.81
1000
= 14 kW
Shaft Power - 14 / 0.50 = 28 Kw
Motor Power - 28 / 0.9 = 31 Kw (considering a motor efficiency of 90%)

## Slide 20: Using oversized pump !
As shown in the drawing, we should be using impeller "E" to do this, but we have an oversized pump so we are using the larger impeller "A" with the pump discharge valve throttled back to 68 cubic meters per hour, giving us an actual head of 76 meters.
Hence, additional power drawn by A over E is 31 –16.1 = 14.9 kW.
Extra energy used - 8760 hrs/yr x 14.9 = 1,30,524 kw.
= Rs. 5,22,096/annum
In this example, the extra cost of the electricity is more than the cost of purchasing a new pump.

## Slide 21
Symptoms that Indicate Potential for Energy Savings |  | 
Symptom | Likely Reason | Best Solutions
Throttle valve-controlled systems | Oversized pump | Trim impeller, smaller impeller, variable speed drive, two speed drive, lower rpm
Bypass line (partially or completely) open | Oversized pump | Trim impeller, smaller impeller, variable speed drive, two speed drive, lower rpm
Multiple parallel pump system with the same number of pumps always operating | Pump use not monitored or controlled | Install controls
Constant pump operation in a batch environment | Wrong system design | On-off controls
High maintenance cost (seals, bearings) | Pump operated far away from BEP | Match pump capacity with system requirement

## Slide 22: Flow vs Speed
If the speed of the impeller is increased from N1 to N2 rpm, the flow rate will increase from Q1 to Q2 as per the given formula:
Flow:
Q1 / Q2 = N1 / N2
Example: 100 / Q2 = 1750/3500
Q2 = 200 m3/hr
  The affinity law for a centrifugal pump with the impeller diameter held constant and the speed changed:

## Slide 23: Head Vs speed
The head developed(H) will be proportional to the square of the quantity discharged, so that
Head:
H1/H2 = (N12) / (N22)
Example: 100 /H2 = 1750 2 / 3500
H2 = 400 m

## Slide 24: Power Vs Speed
The power consumed(W) will be the product of H and Q, and, therefore
Power(kW):
kW1 / kW2 = (N13) / (N23)
Example: 5/kW2 = 17503 / 35003
kW2 = 40

## Slide 25: The affinity law for a centrifugal pump with the speed held constant and the impeller diameter changed
Flow:
Q1 / Q2 = D1 / D2
Example: 100 / Q2 = 8/6
Q2 = 75 m3/hr
Head:
H1/H2 = (D1) x (D1) / (D2) x (D2)
Example: 100 /H2 = 8 x 8 / 6 x 6
H2 = 56.25 m
Horsepower(BHP):
kW1 / kW2 = (D1) x (D1) x (D1) / (D2) x (D2) x (D2)
Example: 5/kW2 = 8 x 8 x 8 / 6 x 6 x 6
kW2 = 2.1 kW

## Slide 26: Effect of speed variation

## Slide 27: Flow Control Strategies Reducing impeller diameter
Changing the impeller diameter gives a proportional change in peripheral velocity
Diameter changes are generally limited to reducing the diameter to about 75% of the maximum, i.e. a head reduction to about 50%
Beyond this, efficiency and NPSH are badly affected
However speed change can be used over a wider range without seriously reducing efficiency
For example reducing the speed by 50% typically results in a reduction of efficiency by 1 or 2 percentage points.
It should be noted that if the change in diameter is more than about 5%, the accuracy of the squared and cubic relationships can fall off and for precise calculations, the pump manufacturer’s performance curves should be referred to

## Slide 28: Impeller Diameter Reduction on Centrifugal Pump Performance

## Slide 29: Pump suction performance (NPSH)
Net Positive Suction Head Available – (NPSHA)
NPSH Required – (NPSHR)
Cavitation
NPSHR increases as the flow through the pump increases
as flow increases in the suction pipework, friction losses also increase, giving a lower NPSHA at the pump suction, both of which give a greater chance that cavitation will occur

## Slide 30: Pump control by varying speed:Pure friction head
Reducing speed in the friction loss system moves the intersection point on the system curve along a line of constant efficiency
The affinity laws are obeyed

## Slide 31: Pump control by varying speed:Static + friction head
Operating point for the pump moves relative to the lines of constant pump efficiency when the speed is changed
The reduction in flow is no longer proportional to speed
A small turn down in speed could give a big reduction in flow rate and pump efficiency
At the lowest speed illustrated, (1184 rpm), the pump does not generate sufficient head to pump any liquid into the system

## Slide 32: Pumps in parallel switched to meet demand

## Slide 33: Pumps in parallel with system curve

## Slide 34: Control of Pump Flow by Changing System Resistance Using a Valve

## Slide 35: Fixed Flow reduction - Impeller trimming
Before Impeller trimming

## Slide 36
After Impeller Trimming

## Slide 37: Meeting variable flow reduction -Variable Speed Drives (VSDs)

## Slide 38: 6.7 Energy Conservation Opportunities in Pumping Systems
Ensure adequate NPSH at site of installation
Operate pumps near best efficiency point.
Modify pumping system/pumps losses to minimize throttling.
Adapt to wide load variation with variable speed drives
Stop running multiple pumps - add an auto-start for an on-line spare or add a booster pump in the problem area.
Conduct water balance to minimise water consumption
Replace old pumps by energy efficient pumps

## Slide 39
Solved Example:
The cooling water circuit of a process industry is depicted in the figure below. Cooling water is pumped to three heat exchangers via pipes A, B and C where flow is throttled depending upon the requirement. The diameter of pipes and measured velocities with non-contact ultrasonic flow meter in each pipe are indicated in the figure.
The following are the other data:
Measured motor power : 50.7 kW
Motor efficiency at operating load : 90%
Pump discharge pressure : 3.4 kg/cm2
Suction head : 2 meters
Determine the efficiency of the pump.

## Slide 40
Flow in pipe A | 22/7 x (0.1)2/4 x 1.5
 | 0.011786 m3/s
Flow in pipe B | 22/7 x (0.1)2/4 x 1.8
 | 0.014143 m3/s
Flow in pipe C | 22/7 x (0.2)2/4 x 2.0
 | 0.062857 m3/s
Total flow | 0.088786 m3/s
Total head | 34 m – 2 m = 32 m
Pump hydraulic power | 0.088786 x 32 x 9.81
 | 27.9 kW
 | 27.9 x 100/50.7 x 0.9
Pump efficiency | 61 %